## How to use the EnergyHub Simulink Model:

Matlab:

What does the model do? And what is it for?

First the setup is intialised in Matlab, declaring all variables. The “setup_V5.m” file hosts different setup strategies, separated by code blocks with comment “%% - name”:

- Initial system sizing

- The entire TGV campus

- No hydrogen

- System sizing improved V1 through V6

The best of the setups was determined to be Improved V4

Each of the setups above is intialised with the variables below, based on data analysis of the system:

SolarPanels             = 12+1.5;                       % [#] (445 Wp)

This is the amount of PV panels accounted for in the model of the energy hub. The existing energy hub has 12 PV panels and virtualized panels to reach 6 kWp capacity (about 1.5 added)

DemandEnergy            = 2200;                         % [kWh]

This is the amount of electric energy that the connected house consumes on a yearly basis in kWh.

HydrogenCapacity        = 48;                           % [kg]

This is the amount of hydrogen that can be stored in the energy hub in kg.

HydrogenStartCapacity   = 0.5*HydrogenCapacity;         % [kg]

This is the amount of hydrogen that is in the buffer during start of the simulation (januari 1st).

% Electrolyser

ElectrolyserWarming = 260;                    % [W] Elec Warming Power

This is the power that the electrolyser consumes during warm-up, during which no hydrogen is produced.

ElectrolyserPower = 2450;                     % [W] Eelc Max Power

This is the power that the electrolyser consumes during max. power, during which hydrogen is produced.

ElectrolyserHyFlow = 510;                     % [NL/h] Hydrogen flow rate at max power

This is the hydrogen that the electrolyser produces during max. power.

ElectrolyserWarmingTime = 12 * 60;            % [s] Warm up time 12 minutes in seconds

This is the time that the electrolyser takes to warm up.

ElectrolyserRampUpTime = 10 * 60;             % [s] Time to go from 60 to 100% = 10 minutes in seconds

This is the time that the electrolyser takes to go from 60 to 100% of max. power.

ElectrolyserRampDownTime = 30 * 60;           % [s] Time to go from 100 to 60%

This is the time that the electrolyser takes to ramp down from 100 to 60%. Of max. power.

ElectrolyserHoldTime = 25 * 60;               % [s] Time before electrolyser actually turns off after off signal

This is the time that the electrolyser stays at 60% power until it is shut off.

% Fuel cell:

FuelCellPower       = 2380;                   % [W] of electricity power (DC), is 1800 (AC) after inverter

This is the DC electricity generation of the fuel cell.

FuelCellHyFlow      = 24;                     % [NL/min] (at full load)

This is the hydrogen consumption of the fuel cell during maximum power generation.

FuelCellStartPower  = 580;                    % [W] of electricity power from start

This is the power production of the fuel right after starting.

FuelCellRampTime1   = 40;                     % [s] Ramp time from 0 to start power

This is the time for the fuel cell to go from 0 to starting power.

FuelCellRampTime2   = 18*60;                  % [s] Ramp time from start power to full power

This is the time for the fuel cell to go from starting power to max. power production.

FuelCellRampDown    = 60;                     % [s] Ramp down from full power to 0 w

This is the time for the fuel cell to go from max. power to 0.

% Battery:

BatteryCapacity     = 15.36;                            % [kWh]

BatteryVNom         = 51.2;                             % [V]

BatteryInitialSoC   = 50;                               % [%]

BatteryCapacity     = 1000*BatteryCapacity/BatteryVNom; % [Ah]

The battery capacity is determined by only the first two variables, BatteryCapacity in kWh, and BatteryVNom in V. It calculates is the remaining parameter(s) accordingly. In the existing case, a 15.36 kWh battery with nominal voltage of 51.2 V is used.

GridExtra           = 0;                                % [W] Extra power to pull from the grid

This is a constant power that we can pull from the grid, could also be exchanged with a timeseries, though some changes would be necessary in the Simulink file.

% BoP:

WinterBase          = 235;                    % [W]

This is the BoP power consumption during Winter when the fuel cell is off.

SummerBase          = 80;                     % [W]

This is the BoP power consumption during Summer when the fuel cell and electrolyser are off.

FuelCellBoP         = 155;                    % [W]

This is the added BoP power consumption during when the fuel cell is on.

FuelCellAirBlower   = 6.4*33.9;               % [W] draws 6.4 [A] directly from MPPT input

This is the BoP power consumption during Winter when the fuel cell is on (only DC air blower).

ElectrolyserBoP     = 80;                     % [W] BoP

This is the BoP power consumption during Summer when the electrolyser is on.

% EMS:

EMSElecStartSoC     = 80;                     % [%] Min SoC to start the electrolyser (was 80)

This is the battery SoC from which the electrolyser is allowed to start.

EMSElecStartHr      = 12;                     % [h] Electrolyser starts before this hour (was 12) 24:00 clock

This is the time limit until the electrolyser is allowed to start.

EMSElecStopSoC      = EMSElecStartSoC-15;     % [%] Min SoC to stop the electrolyser (was 65)

This is the SoC limit until which the electrolyser is allowed to run.

EMSFCStartSoC       = 25;                     % [%] FC starts when this SoC is reached (was 25)

This is the SoC limit from which the fuel cell is turned on.

MSFCStopSoC        = 90;                     % [%] FC stops when this SoC is reached (was 90)

This is the SoC limit from which the fuel cell is turned off.

EMSFCTimeThresholds = [13, 14, 15, 16, 17];   % [13, 14, 15, 16, 17];      % [%] Range of SoC values to turn on FC

EMSFCSoCThresholds  = [40, 50, 60, 70, 80];   % [40, 50, 60, 70, 80];      % [h] Range of time values to turn on FC

These are SoC and time thresholds from which the fuel cell turns on.

MinSoCGrid          = EMSFCStartSoC-5;

This is the SoC limit from which the electricity is pulled from the grid (only occurs when hydrogen buffer is empty).

In the remainder of the code, some PV and demand profile calculations are made, no manual changes here.

% Power & Energy Calculations for demand and PV generation

TitleSize = 18;

FontSize = 14;

Load = readtable("Load.xlsx");      % Loading the data

Load = table2array(Load(:,1:2));    % Loading the data in usable arrays

t = Load(:, 1);                     % Time [s]

PowerNorm = Load(:, 2);             % Normalized power [-]

EnergyHouse = DemandEnergy;          % Household energy use for 1 year for owner-occupied houses in 2021 in NL [kWh] https://www.cbs.nl/en-gb/figures/detail/81528ENG

% Step 1: Calculate the total energy consumption of your normalized load

TotalNormalizedEnergy = sum(PowerNorm) * 1/6;

% Step 2: Scaling factor needed to achieve make the power match the total energy:

ScalingFactor = EnergyHouse / TotalNormalizedEnergy;

% Step 3: Scaling the normalised load power data

LoadPower = PowerNorm * ScalingFactor;

TotalEnergy = sum(LoadPower);       % Energy for 1 year in kWh

% Step 3 (optional): Verify the scaled energy matches EnergyHouse

ScaledTotalEnergy = sum(LoadPower) * 1/6;

time2 = 0:600:365*24*60*60-1;

PDemand = [transpose(time2), LoadPower];  % Combine into one matrix

data = LoadPower*1000;

time = time2;

minlim = 0;

maxlim = 1.1*max(data);

figure('Position', [100 100 1000 600]);

plot(time, data, 'LineWidth',3, 'color', [0.8 0 0])

yline(mean(LoadPower)*1000, 'color' ,[0.3 0.3 0.3], 'LineStyle', '--', LineWidth= 3);

ax = gca;

grid on

title('Residential load power demand profile', 'FontSize',TitleSize)

ylabel('Power [W]', FontSize=FontSize)

xlabel('Time',FontSize=FontSize)

xlim([min(time) max(time)])

ylim([minlim maxlim])

xtick_positions = linspace(min(time), max(time), 12 + 1); % 12 intervals

month_labels = {'Jan', 'Feb', 'Mar', 'Apr', 'May', 'Jun', ...

'Jul', 'Aug', 'Sep', 'Oct', 'Nov', 'Dec'};

ax.XAxis.FontSize = FontSize;

ax.YAxis.FontSize = FontSize;

xticks(xtick_positions);

xticklabels(month_labels);

legend('Power demand','average power','Location', 'northeast', 'FontSize', FontSize);

% Load .mat file

%data = load('Dataframes/Full Year Data/GTImin.mat');

data = load('GTImin.mat');

GTI = data.value_float;

time = 1:60:527026*60-1;

GTIdays = timeseries(GTI, time);

% Convert the time data (if it's in serial date format) to datetime

time = datetime(2024, 1, 1) + minutes(time);

Simulink:

Different Simulink files exist, all based on the latest iteration of the energy hub Simulink file “V5”

- EnergyHub_V5.slx (V5)

- EnergyHub_V5_impr.slx (improved function of V5, changes in EMS)

- EnergyHub_V5_inf_buffer.slx (infinite hydrogen buffer is used here)

- EnergyHub_TGV_Campus.slx (use this for larger systems, it uses better electrolyser control with multiple switchable units)

Inside the Simulink environment multiple interconnected blocks exist.